|  |
| --- |
| **Office of Drinking Water****Third-Party Sanitary Survey Form Checklist** |
| System Name: |  | Survey Date: |  |
| PWS ID#: |  | County: |  | System Type: |  |
| Persons Attending Inspection: |  |
|  |  |
|  |  |
| Inspector’s Name: |  |

|  |
| --- |
| **PART A: SUMMARY OF SIGNIFICANT DEFICIENCIES AND SIGNIFICANT FINDINGS** |
| The following is a completed sanitary survey checklist and summary of inspection findings. This completed sanitary survey checklist is the basis for the cover letter you receive from your local health jurisdiction or from the Washington State Department of Health (DOH). The cover letter documents any significant deficiencies or significant findings that must be corrected. The cover letter may also summarize observations concerning compliance with certain rules and offer recommendations you can use to make improvements to the operation and management of your water system. Contact your DOH regional office with any questions you have about this survey.**Bolded and highlighted** checklist items represent significant deficiencies that, if left uncorrected, create a significant public health risk. Highlighted checklist items represent significant findings that, if left uncorrected, create a significant risk to the physical safety, security, or reliability of the public drinking water supply. You will be required to take some sort of corrective action for each checklist answer that is **bolded and highlighted**, or highlighted. |

|  |
| --- |
| Significant deficiencies and significant findings identified during this sanitary survey: |
|  |
|  |
|  |
|  |
|  |
|  |

|  |
| --- |
| Significant deficiencies or significant findings identified in the previous sanitary survey that remain unaddressed: |
|  |
|  |
|  |
|  |
|  |
|  |

|  |
| --- |
| Observations and recommendations identified during this survey |
|  |
|  |
|  |
|  |
|  |
|  |

|  |
| --- |
| PART B: GENERAL WATER SYSTEM DESCRIPTION |
| Provide a general description of the water system including changes, updates, connections, source(s), storage, number of pressure zones, treatment, and control system(s) and alarm(s). Make corrections and updates to the purveyor’s water facilities inventory form (WFI). |

|  |
| --- |
| PART C: OPERATIONS and MANAGEMENT |
| 1. Was the system operator, who is most knowledgeable about the system’s day-to-day operations, present for the survey?  | [ ] Yes [ ] No [ ] NA |
| 2. Were water system records available for your review? | [ ] Yes [ ] No [ ] Partial |
| 3. Has the purveyor developed and implemented either a Small Water System Management Program or a Water System Plan? | [ ] Yes [ ] No  |
|  3a. If no, are the following planning documents complete and up to date:  |  |
|  | Service Area and Facility Map  | [ ] Yes [ ] No [ ] Partial |
|  | Cross-Connection Control Program  | [ ] Yes [ ] No [ ] Partial |
|  | Source Water Protection Program  | [ ] Yes [ ] No [ ] Partial |
|  | Emergency Response Plan | [ ] Yes [ ] No [ ] Partial |
|  | Operation and Maintenance Program | [ ] Yes [ ] No [ ] Partial |
|  | Coliform Monitoring Plan | [ ] Yes [ ] No [ ] Partial |
|  | Component Inventory and Assessment | [ ] Yes [ ] No [ ] Partial |
|  | Asset Replacement and Other System Improvements | [ ] Yes [ ] No [ ] Partial |
|  | Budget | [ ] Yes [ ] No [ ] Partial |
| 4. Does the purveyor plan to make capital improvements in the next 1-3 years? If yes, describe below | [ ] Yes [ ] No  |
| 5. Is there a backup operator available if the regular one is not available? If yes, provide contact info below | [ ] Yes [ ] No  |
| 6. Were the water system’s current and future water quality monitoring requirements reviewed? | [ ] Yes [ ] No  |
| 7. Was water quality sample results and trends reviewed with the purveyor? | [ ] Yes [ ] No |
| 8. Does the system have emergency power? | [ ] Yes [ ] No |
| 9. Does the system experience frequent power outages (>2 per year)? If yes, explain below | [ ] Yes [ ] No |
| 10. Does the system experience frequent water outages (>2 per year)? If yes, explain below | [ ] Yes [ ] No |
| 11. Does there appear to be adequate reliability provided for this system? If no, explain below | [ ] Yes [ ] No |
| Describe the general level of planning and management documents developed by this water system and any recommendations for additional development, including updates, system management practices and processes, water rates, etc. |

|  |
| --- |
| PART D: SOURCES (This page may be reproduced to add more sources) |
| 12. Did you observe a source connected to the water system that is NOT listed on the WFI and in active use? | [ ] Yes [ ] No |
|  **12a. If so, has the source received written DOH approval? (confirm with DOH post-survey)** | [ ] Yes [ ] **No** |
| 13. DOH Source Number: | SO # | SO # |
| 14. Source Name from the WFI: (For example, North Well; Well #2; ABC334.) |       |       |
| 15. Dept of Ecology Well Tag Number: (Use Well tag ID#, None or Not readable) |       |       |
| 16. Source Use: | P - Permanent | S - Seasonal | E - Emergency |       |       |
| 17. **If this is an emergency source, should it be disconnected?** | [ ] **Yes** [ ] No [ ] NA | [ ] **Yes** [ ] No [ ] NA |
| 18. *Is the source a potential GWI source?*  | *[ ] Yes [ ] No*  | *[ ] Yes [ ] No*  |
| **WELL** (if there is no well, skip to question 34) |  |  |
| **19. Is the Sanitary Control Area (SCA) free of unmitigated potential sources of contamination?** | [ ] Yes **[ ] No** | [ ] Yes [ ] **No** |
| 20. Is the wellhead located in a pit or vault? | [ ] Yes [ ] No | [ ] Yes [ ] No |
| **21. Is the wellhead at risk of submergence?** | [ ] **Yes** [ ] No | [ ] **Yes** [ ] No |
| **22. Is the well cap sealed, watertight, and free of unprotected openings?** | [ ] Yes [ ] **No** | [ ] Yes [ ] **No** |
| **23. Is the well casing free of any unprotected openings?** | [ ] Yes [ ] **No** | [ ] Yes [ ] **No** |
| 24. Is there a vent on the well? | [ ] Yes [ ] No | [ ] Yes [ ] No |
|  **24a. If yes, is the vent protected? (24 non-corrodible mesh screen or slots)** | [ ] Yes [ ] **No** | [ ] Yes [ ] **No** |
| **25. Are conduits and junction boxes sealed to prevent contaminant entry?** | [ ] Yes [ ] **No** | [ ] Yes [ ] **No** |
| 26. Is the well unreasonably at risk to physical damage? | [ ] Yes [ ] No | [ ] Yes [ ] No |
| 27. Is there a raw water source sample tap? | [ ] Yes [ ] No | [ ] Yes [ ] No |
| 28. Is the source metered? | [ ] Yes [ ] No | [ ] Yes [ ] No |
|  28a. If yes, is the source meter read at least monthly? | [ ] Yes [ ] No | [ ] Yes [ ] No |
|  28b. If yes, are the water production records maintained? | [ ] Yes [ ] No | [ ] Yes [ ] No |
| 29. Is the wellhouse properly constructed and maintained? If no, explain below | [ ] Yes [ ] No | [ ] Yes [ ] No |
| 30. Is there any evidence of infestation by rodents or other pests? | [ ] Yes [ ] No | [ ] Yes [ ] No |
| 31. Is the wellhouse and well adequately protected from unauthorized access and tampering? | [ ] Yes [ ] No | [ ] Yes [ ] No |
| 32**. Is there a pump control valve or vacuum relief valve without an air gap on the valve discharge pipe?** | [ ] **Yes** [ ] No [ ] NA | [ ] **Yes** [ ] No [ ] NA |
| **33. Are the source pump and pump controls operational and adequate to prevent chronic water outages or premature pump failure?** If no explain below | [ ] Yes [ ] **No** | [ ] Yes [ ] **No** |
| **SPRING** (if there is no spring, skip to question 41) |  |  |
| **34. Is the springbox (structure, hatch, and overflow) constructed to prevent the entry of contaminants or direct surface drainage?** If yes, describe below. | [ ] Yes [ ] **No** | [ ] Yes [ ] **No** |
| 35. Is there a raw water source sample tap? | [ ] Yes [ ] No | [ ] Yes [ ] No |
| 36. Is the source metered? | [ ] Yes [ ] No | [ ] Yes [ ] No |
|  36a. If yes, is the source meter read at least monthly? | [ ] Yes [ ] No | [ ] Yes [ ] No |
|  36b. If yes, are the water production records maintained? | [ ] Yes [ ] No | [ ] Yes [ ] No |
| 37. Is the springhouse properly constructed and maintained? If no, explain below | [ ] Yes [ ] No | [ ] Yes [ ] No |
| 38. Is there any evidence of infestation by rodents or other pests? | [ ] Yes [ ] No | [ ] Yes [ ] No |
| 39. Is the springhouse and spring box adequately protected from unauthorized access? | [ ] Yes [ ] No | [ ] Yes [ ] No |
| 40.  **Is the Sanitary Control Area (SCA) free of unmitigated potential sources of contamination?**  | [ ] Yes [ ] **No** | [ ] Yes [ ] **No** |
| Describe and evaluate the sourcefacilities including maintenance, operations, sanitary and security observations and any major change made to the source such as pump replacement, deepening or reconstruction: |

|  |
| --- |
| **PART E: DISINFECTION** (*if no disinfection, answer question 41 and skip rest of Part E)* |
| 41. *Does the operator batch chlorinate the source, the distribution system, or the reservoir just before collecting routine or repeat coliform samples? If yes, provide details below.* | [ ] *Yes* [ ] *No* |
| 42. Did you observe disinfection treatment connected to the water system in active use that is NOT listed on the WFI? If yes, explain below | [ ] Yes [ ] No |
| 43. Is ultraviolet light (UV) used for disinfecting a drinking water source? If no, skip to question 46. | [ ] Yes [ ] No |
| 44. Is the UV unit sized for the maximum flow rate, and is there a UV transmittance sensor controlling a solenoid valve or other device to shut off supply if the UV light fails? | [ ] Yes [ ] No |
| 45. Describe the UVequipment including: |  |
| UV manufacturer and model number:      Cleaning frequency of quartz sleeve :       | Rated capacity (gpm):       Mo/Yr UV light last replaced:       |
| 46. Is there continuous chlorination? If no, skip to Part F | [ ] Yes [ ] No |
|  46a. If yes, please measure the free chlorine residual from a representative location in the distribution system. |
| Location description:        | Free chlorine residual:       |
| 47. **Is there a water supply line plumbed directly into a chlorine solution tank without a reduced pressure backflow assembly on the supply line?** | **[ ] Yes** [ ] No |
| 48. Is there a post-treatment sample tap? | **[ ]** Yes [ ] No |
| 49. Does the chlorine compound meet NSF/ANSI Standard 60? | [ ] Yes [ ] No |
| 50. Is a backup chemical feed pump or spare parts for the operating chemical feed pump available onsite? | [ ] Yes [ ] No |
| 51. According to the operator, is there a DOH requirement for Chlorine Contact Time? If no, skip to Part F | [ ] Yes [ ] No |
|  51a. *If yes, measure and record the free chlorine residual at the CT6 compliance location:* *Describe compliance sampling location below – location must be prior to the first service connection downstream of chlorine addition.* |
| 52. *Is the chlorine pump and pump controls constructed and maintained to provide uninterrupted, reliable CT6 treatment? If no, describe below.* | [ ] *Yes* [ ] *No* |
| Describe the chlorinationfacilities including purpose for chlorination, concerns with maintenance or operations, purveyor’s record keeping of monthly reports, and sanitary and security observations: |
|  |

|  |
| --- |
| **PART F: TREATMENT**  |
| 53. Is there any treatment other than chlorination or UV in use? If no, skip Part F.  | [ ] Yes [ ] No  |
| 54. Did you observe a treatment process connected to the water system in active use that is NOT listed on the WFI? If yes, describe below. | [ ] Yes [ ] No  |
| 55. **Is there a water supply line plumbed directly into a chemical solution tank (e.g., fluoride saturator) without a reduced pressure backflow assembly on the supply line?**  | [ ] **Yes** [ ] No [ ] NA |
| **56. Are primary contaminant treatment facilities (e.g., nitrate, corrosion control, arsenic) operating properly?** If no, describe below | [ ] Yes [ ] **No**  |
| 57. Do the water treatment chemicals meet NSF/ANSI Standard 60?  | [ ] Yes [ ] No [ ] NA |
| 58. Is there a post-treatment sample tap? | **[ ]** Yes [ ] No |
| Describe the treatmentfacilities including purpose for treatment, concerns with maintenance or operations, purveyor’s record keeping of monthly reports, and sanitary and security observations: |

|  |
| --- |
| **PART G: BOOSTER PUMPING FACILITIES and CONTROLS** |
| 59. Are there any booster pumps in use? If no, skip Part G | [ ] Yes [ ] No |
| 60. Are the booster pumps in good working condition? If no, explain below | [ ] Yes [ ] No |
| **61. Are pump and pump controls operational and adequate to prevent chronic water outages or premature pump failure?**  If no explain below | [ ] Yes [ ] **No** |
| 62. If there is a booster pump house/pump station, is it secure against unauthorized entry? If no, explain below | [ ] Yes [ ] **No** [ ] NA |
| 63. Is the booster pump house/pump station properly constructed and maintained? If no, explain below | [ ] Yes [ ] No |
| Describe and evaluate the pump facilities and controls including maintenance, operations, sanitary and security observations: |

|  |
| --- |
| **PART H: PRESSURE TANKS** |
| 64. Are there any pressure tanks in use? If no, skip Part H | [ ] Yes [ ] No |
| 65. For systems using an air compressor, is the compressor an oil-free type or does it use food-grade oil?  | [ ] Yes [ ] No [ ] NA |
| 66. Are valves present to isolate pressure tanks for maintenance or repair?  | [ ] Yes [ ] No |
| 67. Is there an ASME pressure relief valve installed between each pressure tank and any shutoff valve? (see DOH publication #331-429) | [ ] Yes [ ] No |
| 68. Are the pressure tanks in good working condition? If no, explain below | [ ] Yes [ ] No |
| Describe and evaluate the pressure tanks including maintenance, operational, sanitary and security observations: |

|  |
| --- |
| **PART I: FINISHED WATER STORAGE** |
| 69. Is there a finished water storage tank in use? If no, skip Part I | [ ] Yes [ ] No |
| 70. If unable to physically inspect the storage tank hatch, vent, roof, or overflow outlet, select the method you discussed with the purveyor to document their condition: |
| a | [ ]  Reviewed and discussed maintenance records and recent photos |
| b | [ ]  Photos will be taken and mailed by purveyor; additional follow-up required by DOH |
| c | [ ]  Purveyor unable or unwilling to document; additional follow-up required by DOH |
| Insert Tank Names |       |       |
| 71. Is the storage tank protected from unauthorized entry or vandalism? If no, explain below | [ ] Yes [ ] No [ ] unk | [ ] Yes [ ] No [ ] unk |
| **72. Is the reservoir roof free of any unprotected openings?** If no, explain below | [ ] Yes [ ] **No** [ ] unk | [ ] Yes [ ] **No** [ ] unk |
| **73. Is the access hatch constructed and sealed to prevent the entry of contaminants?** If no, explain below | [ ] Yes [ ] **No** [ ] unk | [ ] Yes [ ] **No** [ ] unk |
| 74. If able to open hatch, is the stored water free of visible contaminants? If no, explain below | [ ] Yes [ ] No [ ] unk | [ ] Yes [ ] No [ ] unk |
| 75. Is there a dedicated air vent on the storage tank? | [ ] Yes [ ] No [ ] unk | [ ] Yes [ ] No [ ] unk |
|  **75a. If yes, is the air vent constructed to prevent the entry of contaminants?** If no, explain below | [ ] Yes [ ] **No** [ ] unk | [ ] Yes [ ] **No** [ ] unk |
| **76. Is the overflow line constructed to prevent contaminants from entering the tank?** If no, explain below | [ ] Yes [ ] **No** [ ] unk | [ ] Yes [ ] **No** [ ] unk |
| 77. Does the overflow line discharge near ground level? | [ ] Yes [ ] No [ ] unk | [ ] Yes [ ] No [ ] unk |
| 78. Is the overflow line discharge area protected from potential erosion? | [ ] Yes [ ] No [ ] unk | [ ] Yes [ ] No [ ] unk |
| 79. Does the overflow line discharge into a storm drain or surface water?  | [ ] Yes [ ] No [ ] unk | [ ] Yes [ ] No [ ] unk |
|  **79a. If yes, is there an air gap at the discharge of the overflow OR does the overflow drop at least 34 vertical feet measured from the overflow connection to the reservoir down to the receiving water body?** | [ ] Yes [ ] **No** [ ] unk | [ ] Yes [ ] **No** [ ] unk |
| **80.** **Does the overflow line discharge directly into a sanitary sewer without an air gap?** | [ ] **Yes** [ ] No [ ] unk | [ ] **Yes** [ ] No [ ] unk |
| 81. Can the reservoir be isolated from the rest of the water system and be drained through a dedicated drain line? | [ ] Yes [ ] No [ ] unk | [ ] Yes [ ] No [ ] unk |
| 82. When was the tank inspected last? Explain below if necessary |       |       |
| 83. What is the tank cleaning frequency? Explain below if necessary |       |       |
| 84. Does the tank size, operation, and internal piping configuration appear to provide adequate water turnover (i.e. separate inlet/outlet, baffling or mixing to reduce stagnant water)? If no, explain below | [ ] Yes [ ] No [ ] unk | [ ] Yes [ ] No [ ] unk |
| 85. Does the tank show signs of excessive leakage, significant structural cracking, or an advanced concrete spalling? | [ ] Yes [ ] No | [ ] Yes [ ] No |
| Describe and evaluate the finished water storage facilities including volume, operational drawdown, configuration of the inlet/outlet piping, any concerns about operations and maintenance, and sanitary and security observations: |

|  |
| --- |
| **PART J: DISTRIBUTION SYSTEM** |
| 86. Is a complete, up to date and accurate map of the distribution system maintained? | [ ] Yes [ ] No  |
| 87. *Does the system provide adequate pressure throughout the distribution system? If no, explain below.* | [ ] Yes [ ] No |
| 88. Are proper procedures followed for disinfection of new construction or repairs? | [ ] Yes [ ] No |
| 89. *Are there any air relief or vacuum relief valves subject to submersion?* | [ ] Yes [ ] No |
| 90. Does the purveyor seasonally or annually flush the distribution system? If yes, describe below | [ ] Yes [ ] No |
| 91. Does the purveyor exercise its distribution system valves? If yes, describe below | [ ] Yes [ ] No |
| Describe and evaluate the distribution system including maintenance, operational, sanitary and security observations: |

|  |
| --- |
| **PART K: CROSS CONNECTION CONTROL (CCC)** |
| 92. Does the water system serve a single connection? If yes, refer the purveyor to the Uniform Plumbing Code and skip Part K  | [ ] Yes [ ] No |
| 93. Is the water system known to serve one or more high health hazard premises, such as those listed in Table 13 in WAC 246-290-490? If yes, describe the premise(s) below. | [ ] Yes [ ] No |
| 94. Has the purveyor established the legal authority to implement a CCC program (i.e., formally adopted an ordinance, resolution, by-laws, or other document defining the purveyor’s CCC program requirements, and empowering the purveyor to enforce them)? | [ ] Yes [ ] No |
| 95. Has the purveyor designated a CCC Specialist (CCS) to be in responsible charge of the CCC program? | [ ] Yes [ ] No  |
|  95a. If yes, has the CCS conducted a hazard evaluation to identify high health hazard premises? | [ ] Yes [ ] No  |
|  95b. If yes, has the purveyor completed installation of a backflow prevention assembly on the service line to each identified high health hazard premise? | [ ] Yes [ ] No [ ] NA |
| 96. Has each testable backflow prevention assembly installed for premises isolation been tested by a DOH certified backflow assembly tester (BAT) within the past 12 months? | [ ] Yes [ ] No [ ] NA |
| **97. Did you observe the end of a hose connected to the potable water system submerged in a pool, hot tub, watering trough, or other non-potable body of water observed during the survey?** | [ ] **Yes** [ ] No |
| **98. This question only applies to a facility operating a sewage dump station: Is there a sewage dump station without a reduced pressure backflow assembly on the water supply at the dump station?** | [ ] **Yes** [ ] No [ ] NA |
| Additional cross connection control program comments: |

|  |
| --- |
| **PART L: OPERATOR** |
| 99. Is the operator of the water system certified? | [ ] Yes [ ] No |
| 100. Describe the operator’s certification level (if certified), duration of employment with this water system, relationship with the system (e.g., contract operator, SMA, direct hire employee, volunteer, temporary, or owner), and duties and responsibilities. |
| 101. Does the operator conduct self-inspections of the water system? If yes, describe frequency and scope of these self-inspections below. | [ ] Yes [ ] No |
| 102. *Is the operator performing measurements and calibration of water treatment monitoring equipment consistent with manufacturer recommendations? If no, describe below.* | [ ] Yes [ ] No [ ] NA |
| 103. *Is the operator using proper inputs to treatment plant operations reports, such as correct volume, peak flow rate, time, and making the proper calculations? If no, describe below.* | [ ] Yes [ ] No [ ] NA |
| 104. *Does the operator take compliance water quality samples at the proper location? If no, describe below.* | [ ] Yes [ ] No [ ] NA |
| Additional operator comments: |

|  |
| --- |
| **PART M: FIELD NOTES AND OTHER** |
| Descriptions of any water quality tests, physical measurements, or simple repairs completed during the inspection:      |

|  |
| --- |
| **PART N: SUPPLEMENTAL NOTES AND SAFETY CONCERNS** |
| Supplemental comments from other parts of the checklist, and documentation of field safety concerns: |



To request this document in another format, call 1-800-525-0127. Deaf or hard of hearing customers, please call 711 (Washington Relay) or email doh.information@doh.wa.gov. If in need of translation services, call 1-800-525-0127.

|  |
| --- |
| **PART O: WATER SYSTEM FACILITIES FIELD SCHEMATIC** |
| Use the space below to sketch a simple schematic of the water system facilities. You may use the templates shown below to help build your schematic. The sketch should show location of sources, treatment, pressure tanks, booster pumps, storage tanks, and a simple representation of the distribution system. Include direction of flow (directional arrows) and brief description of how the controls function. |
| Source Name: |  | Source Number: |  |
| Example templates you can use to build your schematic:🏠PressureSwitchDistributionSystemBoosterPumpPressureTankChlorineInjection PointReservoir |
|  |
| Booster PumpsSample TapCartridgeFiltrationIon exchangePressure TankMeterReservoir |

|  |
| --- |
| **PART P: INVENTORY OF POTENTIAL SOURCES OF CONTAMINANTS WITHIN THE SANITARY CONTROL AREA** |
| Use the graph below to locate any potential biological and chemical contaminants found within the source’s Sanitary Control Area (SCA). The SCA is the protective area within 100 feet of wells or 200 feet of springs. |
| Source Name: |  | Source Number: |  |



|  |
| --- |
| **Radius (select one)** |
| [ ]  | 100 ft for Wells |
| [ ]  | 200 ft for Springs |

|  |
| --- |
| **Description of Features Shown on the SCA Schematic** |
| A. |       | C. |       | E. |       |
| B. |       | D. |       | F. |       |
| **Sources of Contamination** | **Feet** | **Sources of Contamination** | **Feet** | **Sources of Contamination** | **Feet** |
| Abandoned water wells |       | Dumpsters |       | Pesticide storage |       |
| Animal burial |       | Fuel tanks (above or below ground) |       | Roads and parking lots |       |
| Biological contaminants |       | Graveyards |       | Sewer lines, gravity or pressure |       |
| Buildings |       | Hazardous waste disposal site |       | Storm water catch basins |       |
| Chemical contaminants |       | Hazardous waste facility |       | Surface water |       |
| Drainfields and septic tanks |       | Irrigation canal |       | Wastewater spray irrigation |       |
| Drug lab |       | Landfill, dump, disposal area |       | Other:      |
| Dry wells |       | Pesticide application |       |